## Load Calculation
Power People Electric
Jason Summers
Lic: TMEL #12345
LOAD CALCULATION REPORT
NEC 2023 - Standard Method Calculation
PROJECT ADDRESS |  |  |  | CLIENT NAME
123 Somewhere St., Richmond, TX |  |  |  | Marianne Doe
CALCULATION DATE | 2026-01-23T22:18:56.859Z
Lighting and Receptacles | [7 empty] | NEC 220.12
Dwelling area |  |  | 2560 |  | sq ft
|  | × | 3 |  | VA/sq ft
General lighting load |  | = |  |  |  | = | 7680 |  | VA
SECTION SUBTOTAL | [7 empty] | 7680 |  | VA
Line Load | [7 empty] | 7680 |  | VA
Neutral Load | [7 empty] | 7680 |  | VA
Small Appliances & Laundry | [7 empty] | NEC 220.52(A)
Number of circuits |  |  | 4
|  | × | 1500 |  | VA
Small appliance load |  | = |  |  |  | = | 6000 |  | VA
SECTION SUBTOTAL | [7 empty] | 6000 |  | VA
Line Load | [7 empty] | 6000 |  | VA
Neutral Load | [7 empty] | 6000 |  | VA
Apply Demand Factors | [7 empty] | NEC 220.42
Total general lighting + small appliance |  |  | 13680 |  | VA
First 3,000 VA @ 100% |  |  | 3000 |  | VA
Next 117,000 VA @ 35% |  | + | 3738 |  | VA
Remaining @ 25% |  | + | 0 |  | VA
Net computed load |  | = |  |  |  | = | 6738 |  | VA
SECTION SUBTOTAL | [7 empty] | 6738 |  | VA
Line Load | [7 empty] | 6738 |  | VA
Neutral Load | [7 empty] | 6738 |  | VA
Fixed Appliances | [7 empty] | NEC 220.53
Number of appliances |  |  |  |  | 4
Total nameplate rating |  |  |  |  | 7350 |  |  |  | VA
Dishwasher |  |  |  |  | 1200 |  |  |  | VA
Disposal |  |  |  |  | 850 |  |  |  | VA
Water Heater |  |  |  |  | 1300 |  |  |  | VA
Pool Pump |  |  |  |  | 4000 |  |  |  | VA
Demand factor |  |  |  |  | 75%
Fixed appliance load |  |  |  |  | 5512.5 |  |  |  | VA
SECTION SUBTOTAL | [7 empty] | 5512.5 |  | VA
Line Load | [7 empty] | 5512.5 |  | VA
Neutral Load | [7 empty] | 5512.5 |  | VA
Electric Dryers | [7 empty] | NEC 220.54
Dryer load (5kW minimum) |  |  | 5000 |  | VA
Dryer |  |  | 5000 |  | VA
Demand factor (1 units) |  | × | 100%
Calculated dryer load |  | = |  |  |  | = | 5000 |  | VA
Neutral load (70%) |  |  | 3500 |  | VA
SECTION SUBTOTAL | [7 empty] | 5000 |  | VA
Line Load | [7 empty] | 5000 |  | VA
Neutral Load | [7 empty] | 3500 |  | VA
Cooking Appliances | [7 empty] | NEC 220.55
Cooking demand |  |  | 4050 |  | VA
Oven |  |  | 3400 |  | VA
Range |  |  | 2000 |  | VA
Neutral load (70%) |  |  | 2835 |  | VA
SECTION SUBTOTAL | [7 empty] | 4050 |  | VA
Line Load | [7 empty] | 4050 |  | VA
Neutral Load | [7 empty] | 2835 |  | VA
HVAC | [7 empty] | NEC 220.60
AC load |  |  | 6000 |  | VA
Heating load |  |  | 3000 |  | VA
Selected (AC) |  | = |  |  |  | = | 6000 |  | VA
SECTION SUBTOTAL | [7 empty] | 6000 |  | VA
Line Load | [7 empty] | 6000 |  | VA
Neutral Load | [7 empty] | 0 |  | VA
Largest Motor | [7 empty] | NEC 220.50
Largest motor |  |  | 6000 |  | VA
Source: HVAC equipment |  |  | 6000 |  | VA
25% addition |  | × | 1500 |  | VA
SECTION SUBTOTAL | [7 empty] | 1500 |  | VA
Line Load | [7 empty] | 1500 |  | VA
Neutral Load | [7 empty] | 0 |  | VA
EVSE | [7 empty] | NEC 220.57
Number of units |  |  | 1
EVSE Unit |  |  | 9000 |  | VA
EVSE load |  |  | 9000 |  | VA
SECTION SUBTOTAL | [7 empty] | 9000 |  | VA
Line Load | [7 empty] | 9000 |  | VA
Neutral Load | [7 empty] | 0 |  | VA
SERVICE LOAD SUMMARY
Total Line Demand Load | [6 empty] | 37800.5 |  | VA
Total Neutral Demand Load | [6 empty] | 18585.5 |  | VA
Required Service Ampacity (@ 240V) | [6 empty] | 158 |  | AMPS